## Sheet1
TRACEv7 Recommendation. Version: 0.1 Date (YMD): 2016-01-13
Cooling Towers
Attributes | Rating
Energy Savings Potential (kWh) | 50000
Percent Energy Saving Range % | 30% - 50%
CAPEX or First Cost ($) | $200/Ton - $220 /Ton at 3 GPM/Ton @ 78°F Wet Bulb Approach)
Speed of Implementation (Years) | 1
Co-benefits | Minimum water consumption Improved microbiological control Extended lifespan, which is more economical option for business owners Both latent and sensible heat transfer Less volume of air to reject heat load (less energy used than fans) Increasing the efficiency of heat transfer Smaller equipment sizes for the same capacity
CSF Factor | Rating
Finance | Medium
Human Resources | Low
Assets & Infrastructure | Medium
Data and Information | Medium
Policy Regulation and Enforcement | Medium
Description | Summary
Description | A cooling tower is a specialized heat exchanger where air and water are brought in direct contact with each other in order to reduce the water’s temperature. The aim of this recommendation is to assess how a municipality can support the replacement of conventional air cooling systems with water cooling towers in commercial and residential buildings .. Evaporative water-cooled systems consume approximately half the overall energy of comparably sized air-cooled systems, yielding substantial lifecycle cost savings. Low energy consumption is not only a financial victory for the building owner, but also helps to respect and preserve the environment by reducing greenhouse gas emissions from supporting power plants. Lower system temperatures and pressures also reduce system maintenance and extend the life of the mechanical equipment.
Description | Summary
Description | A cooling tower is a specialized heat exchanger where air and water are brought in direct contact with each other in order to reduce the water’s temperature. The aim of this recommendation is to assess how a municipality can support the replacement of conventional air cooling systems with water cooling towers in commercial and residential buildings .. Evaporative water-cooled systems consume approximately half the overall energy of comparably sized air-cooled systems, yielding substantial lifecycle cost savings. Low energy consumption is not only a financial victory for the building owner, but also helps to respect and preserve the environment by reducing greenhouse gas emissions from supporting power plants. Lower system temperatures and pressures also reduce system maintenance and extend the life of the mechanical equipment.
Activity | Process
Monitoring | Monitoring the progression and effectiveness of recommendations, once implemented, is fundamental to an accurate understanding of their value over the longer term. Where the City Authority (CA) implements a recommendation, Key Performance Indicators (KPIs) should be defined to track performance and a target (or set of targets) should be defined to ensure the expected progress over a given timescale. At the same time a monitoring plan should be designed. The monitoring plan does not need to be complicated or time consuming but should, as a minimum, cover the following aspects: identification of information sources, identification of the key performance indicators, a means of measurement and validating measuring equipment or processes, record keeping protocols, a schedule for measurement activity (daily, weekly, monthly etc.), assignment of responsibilities for each aspect of the process, a means of auditing and reviewing performance and finally, establishment of reporting and review cycles.
Key Performance Indicator | Some suggested key performance indicators that relate specifically to this recommendation include: Efficiency: Gallons per Minute/Horsepower (GPM/HP) Energy Savings: kWh/annum Optimized System Energy: kW/ton of refrigeration
Example and Links | Summary
Water cooled Chiller System, | The Baltimore Aircoil Company conducted a study on the design of chillers with lower condenser water flow rates and a higher range in order to improve system lifecycle costs when replacing air cooled condensers in refrigeration units. Typically water-cooled chiller systems have been designed around condenser water entering the cooling tower at temperatures of 85°F with a nominal condenser water flow of 3 US gallons per minute (USGPM) per ton and a 10°F range. The study investigated the efficiency of chilled water systems by focusing on two parameters: approach (the temperature difference between the water leaving the tower and the wet bulb temperature of the entering air) and design wet bulb. Furthermore, in considering these parameters, the study illustrated different optimized first costs to show levels of efficiency. This process was repeated for magnitudes of loadings and various approach temperatures. This study selected cooling towers with the same 10°F range of water entering the tower and 3.0 USGPM/ton at a 7°F range approach. . The study concluded that lower flow system can deliver improved operating costs as well as a reduction in energy usage by utilizing smaller pumps and cooling tower fan motors. It was found that typical first costs for cooling towers range between $200/Ton and $220 /Ton for a chiller that is designed at 3 GPM/Ton @ 78°F Wet Bulb Approach.
Improving Energy Efficiency in Cooling Tower Design | Marley, a cooling tower manufacturer published a presentation on the environmental impacts of cooling towers and the methods available to improve cooling tower efficiency. The presentation emphasized on optimizing and utilizing water cooled systems. Water cooled systems provide the largest opportunity to reduce energy use. When comparing to an air cooled system, water cooled systems have lower condensing temperatures, 1.5 to 3 times greater Coefficient of Performance (COP) than air cooled, and 30 to 50% potential energy savings. The study concluded that designing cooling towers with outlet water temperatures as low as possible would result in increased efficiency of 1 to 3% for every 1°C.
Tool and Links | Summary
Cooling Tower Efficiency Guide | Environmental Defense Fund + Business. 2013. Cooling Tower Efficiency Guide.
Water Conservation in Cooling Towers | The Australian Institute for Refrigeration, Air Conditioning and Heating. 2009. Water Conservation in Cooling Towers